KEYSTONE F89 PNEUMATIC QUARTER-TURN ACTUATOR

# GENERAL PURPOSE / HAZARDOUS AREA

## FEATURES

- Direct mounting to all Keystone butterfly valves and ball valves.

- Valve connection compatible with Keystone (imperial and metric) and ISO 5211.

- Double Rack and Pinion design nullifies side loads on the pinion shaft, minimizing bearing wear and extending life.

- Optimized product flow with standard mounted travel stops for valve position adjustment in open and close position (+/- 5° at each end).

- Anodized aluminium body with electrostatic powder coating (ESPC) finish provides durable protection against corrosive environments.

- Double acting and spring return versions available for cost effective and safe operation.

- Up to 12 individual springs offer flexible torque range for both ball as butterfly valves.

- Pre-compressed spring design and anti-blowout drive pinion means safe maintenance and operation.

## MATERIALS

Body:	Extruded aluminium (ESPC coated) End caps: Cast aluminium (ESPC coated)

## MOUNTING SPECIFICATIONS

Actuator to valve: ISO and Keystone standard Accessories:	Namur VDI/VDE 3845

## PERFORMANCE DATA

The F89 actuator meets the EN15714-3 requirements and has been validated for a lifetime up to 500,000 cycles under the specified conditions.

## TECHNICAL DATA

Torque output range:

Double acting:	11 - 4173 Nm (97 - 36955 in·lb)

Spring return:	6 - 1663 Nm (51 - 14729 in·lb)

Operating medium: Compressed air

(dry or lubricated)

Air supply pressure: 8.3 bar (120 psi) max. dynamic

10 bar (145 psi) max. static Travel adjustment: +/- 5° at each end of travel

0-100% travel stop available on request

Temperature range: -20°C to +80°C

(-4°F to +176°F)

Low temp version: -52°C to +65°C

(-62°F to +149°F)

High temp version: -15°C to +150°C

(5°F to +302°F)

Certification:	ATEX II 2 GD IIC T6

## PRINCIPLE OF OPERATION

Both the double acting and spring return actuators feature a compact design each with their own set of end caps. The unit can be converted from double acting to single acting (or reverse) in the field without the requirement of special tools. The spring return actuator is available with spring sets representing 2.8 bar (40 psi) to 8.3 bar (120 psi) in 0.7 bar (10 psi) increments.

The springs are manufactured from heavy gauge wire to assure long life and ESPC coated for corrosion resistance. They are pre-compressed using a special container to ensure safe operation and maintenance.

## DOUBLE ACTING

To open valve

In a double acting application, air pressure is introduced to Port 2 (A), pressurizing the space between the pistons and driving the pistons out towards the actuator ends. The volume

of air above the piston heads is exhausted to atmosphere. This causes the piston racks to drive the pinion in a counterclockwise direction,

The dual-keyed output shaft allows parallel or perpendicular mounting to the valve flow direction. In normal conditions the actuator is mounted in parallel with the valve flow direction, operating in a counter clockwise (CCW) rotation from the closed to the open position.

The standard operation direction of the spring fail close action is clockwise (CW). By rotating the pistons 180 degrees in the body in relation to the pinion, the actuator operation direction can be reversed. Although rotating the actuator 90 degrees will have a similar effect, the piston rotation is preferred as it maintains the parallel mounting and keeps the valve operation in

the correct quadrant.

resulting in a quarterturn rotation. This rotation is transferred to the valve shaft, opening the valve.

## To close valve

Air pressure introduced to Port 4 (B), pressurizes the spaces above each piston head and drives the pistons inward. The volume

of air between the pistons is exhausted to atmosphere. This causes the piston racks to drive the pinion in a clockwise direction, resulting in a quarter-turn rotation.

This rotation is transferred to the valve shaft, closing the valve.

4 (B)	2 (A)

Exhaust	Air in

4 (B)	2 (A)

Air in	Exhaust

## SPRING RETURN

To open valve

In a single acting application, air pressure is introduced to Port 2 (A), pressurizing the space between the pistons and driving the pistons out towards the actuator ends while at the same

time compressing the springs.	 	 This causes the piston racks to drive the pinion

in a counterclockwise direction, resulting in a quarter-turn rotation. This rotation is

transferred to the valve shaft, opening the valve.

## To close valve

When the air pressure is relieved, the spring tension moves the pistons inward and exhausts the air through Port 2 (A). This causes the piston racks to drive the pinion in a clockwise

direction, resulting in a quarter-turn rotation.	 	 This rotation is transferred to the valve shaft,

closing the valve.

4 (B)	2 (A)

Vent port	Air in

4 (B)	2 (A)

Vent port	Exhaust

## TRAVEL ADJUSTMENT

Within the mechanical connections of the drive between the valve and the actuator there are several points of manufacturing tolerance, including valve disc or ball to stem, stem to adapter, and adapter to actuator that must

be compensated for in the operation of the assembly. Therefore, adjustment is necessary to ensure that valve operation is as precise as required. The F89 dual travel stops allow +/-5° adjustment at both ends of the stroke, resulting in a total stroke range of 80° to 100° rotation. For special applications an optional linear travel stop is available, which reduces

the stroke from 0-100%.

## Resilient seated butterfly valves

Shut-off occurs before the disc has rotated a full 90° from the open position. Travel adjustment is therefore desirable to prevent over travel, which would result in

unnecessary operating torque and premature deterioration of seat life. In the open position, adjustment is necessary to ensure maximum flow through the valve and minimum dynamic forces acting on the disc.

## High performance butterfly valves

The double offset design of high performance butterfly valves results in the disc moving into the seat with a camming action. It is important that the disc does not travel beyond the seat position, otherwise damage to the seat will occur.

## Ball and plug valves

The ball or plug must be precisely in line with the valve port to prevent damage to the seat in the open position. Adjustment at the closed position is necessary to ensure that complete shut-off is achieved.

## DIMENSIONS

Top view model 002 – 020

A1

A2

C

H

J

Side view

D

E

## TABLE 1 - DIMENSIONS F89 METRIC (mm)

Top view model 032 – 240

H

J

Front view

B

| Model F89-002 | A1 (1) - | A2 (1) 121 | B 72 | C 74 | D 54 | E 66 | Top of shaft (2) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | H | J Key |  |
|  |  |  |  |  |  |  | 16.0 | 11.0 |  |
| F89-003 | 186 | 125 | 86 | 81 | 59 | 79 | 16.0 | 11.0 |  |
| F89-004 | 217 | 143 | 96 | 91 | 61 | 80 | 16.0 | 11.0 |  |
| F89-006 | 259 | 169 | 101 | 108 | 64 | 87 | 16.0 | 11.0 |  |
| F89-009 | 257 | 174 | 119 | 124 | 64 | 99 | 16.0 | 11.0 |  |
| F89-014 | 307 | 193 | 138 | 141 | 78 | 112 | 16.0 | 11.0 |  |
| F89-020 | 378 | 236 | 155 | 157 | 81 | 123 | 16.0 | 11.0 |  |
| F89-032/033 | 462 | 283 | 171 | 182 | 95 | 136 | 20.6 | 21.6 | 4.8 |
| F89-051/052 | 476 | 298 | 213 | 210 | 111 | 159 | 20.6 | 21.6 | 4.8 |
| F89-084/085/086 | 627 | 384 | 227 | 233 | 130 | 190 | 25.4 | 27.0 | 6.4 |
| F89-139/140/141 | 726 | 431 | 274 | 288 | 154 | 233 | 25.4 | 27.0 | 6.4 |
| F89-240 | 845 | 507 | 325 | 341 | 186 | 290 | 25.4 | 27.0 | 6.4 |

## TABLE 2 - DIMENSIONS F89 IMPERIAL (in)

| Model F89-002 | A1 (1) - | A2 (1) 4.76 | B 2.83 | C 2.91 | D 2.13 | E 2.60 | Top of shaft (2) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | H | J Key |  |
|  |  |  |  |  |  |  | ⅝ | 7/16 |  |
| F89-003 | 7.30 | 4.90 | 3.39 | 3.18 | 2.32 | 3.09 | ⅝ | 7/16 |  |
| F89-004 | 8.53 | 5.63 | 3.78 | 3.60 | 2.40 | 3.15 | ⅝ | 7/16 |  |
| F89-006 | 10.20 | 6.65 | 3.97 | 4.26 | 2.52 | 3.42 | ⅝ | 7/16 |  |
| F89-009 | 10.10 | 6.85 | 4.69 | 4.87 | 2.52 | 3.91 | ⅝ | 7/16 |  |
| F89-014 | 12.07 | 7.60 | 5.42 | 5.55 | 3.07 | 4.41 | ⅝ | 7/16 |  |
| F89-020 | 14.89 | 9.29 | 6.10 | 6.20 | 3.19 | 4.82 | ⅝ | 7/16 |  |
| F89-032/033 | 18.20 | 11.14 | 6.73 | 7.18 | 3.74 | 5.35 | 0.81 | 0.84 | 0.19 |
| F89-051/052 | 18.72 | 11.73 | 8.37 | 8.25 | 4.37 | 6.26 | 0.81 | 0.84 | 0.19 |
| F89-084/085/086 | 24.69 | 15.12 | 8.94 | 9.17 | 5.12 | 7.48 | 1.00 | 1.06 | 0.25 |
| F89-139/140/141 | 28.58 | 16.97 | 10.79 | 11.34 | 6.06 | 9.17 | 1.00 | 1.06 | 0.25 |
| F89-240 | 33.27 | 19.96 | 12.80 | 13.43 | 7.32 | 11.42 | 1.00 | 1.06 | 0.25 |

NOTES

- A1 = spring return; A2 = double acting

- All actuators have either DD 16.0 x 11.0 (DD ⅝ x 7/16) top shaft connection or a plastic insert to this dimension, for direct mounting of switchbox accessories. Indicated values are actual pinion top dimensions.

## DIMENSIONS

Pinion connection F89E sizes 002-020	Pinion connection F89E sizes 032-240

G

F

K

Ø F

The F89 actuator is available with 4 different valve connections: F89D - ISO 5211 (metric threaded); F89E - Keystone ISO (metric threaded); F89U - Keystone imperial + metric threaded

## TABLE 3A - VALVE CONNECTION ISO FLANGE (mm)

| Model F89-002 | F89E - Keystone ISO F89D - ISO 5211 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | F | Bottom of shaft G Key PCD |  |  | Mounting holes No x Size x Depth | Bottom of shaft Drive: Star no | PCD | Mounting holes No x Size x Depth |
|  | 16.0 | 11.0 |  | F03 F05 | 4x M5 x 8.0 4x M6 x 10.0 | ** | F03 F05 | 4x M5 x 8.0 4x M6 x 10.0 |
| F89-003 | 16.0 | 11.0 |  | F05 F07 | 4x M6 x 10.0 4x M8 x 13.0 | 14 | F05 F07 | 4x M6 x 10.0 4x M8 x 13.0 |
| F89-004 | 16.0 | 11.0 |  | F05 F07 | 4x M6 x 10.0 4x M8 x 13.0 | 14 | F05 F07 | 4x M6 x 10.0 4x M8 x 13.0 |
| F89-006 | 20.0 | 14.0 |  | F05 F07 | 4x M6 x 10.0 4x M8 x 13.0 | 17 | F05 F07 | 4x M6 x 10.0 4x M8 x 13.0 |
| F89-009 | 20.0 | 14.0 |  | F05 F07 | 4x M6 x 10.0 4x M8 x 13.0 | 17 | F05 F07 | 4x M6 x 10.0 4x M8 x 13.0 |
| F89-014 | 20.0 | 14.0 |  | F07 | 4x M8 x 13.0 | 17 | F07 | 4x M8 x 13.0 |
| F89-020 | 25.0 | 18.0 |  | F07 F10 F12 | 4x M8 x 13.0 4x M10 x 15.0 4x M12 x 19.0 | 22 | F07 F10 F12 | 4x M8 x 13.0 4x M10 x 15.0 4x M12 x 19.0 |
| F89-032 | 35.0 10 x 8 |  |  | F10 F12 | 4x M10 x 15.0 4x M12 x 19.0 | 27 | F10 F12 | 4x M10 x 15.0 4x M12 x 19.0 |
| F89-052 | 35.0 10 x 8 |  |  | F10 F12 | 4x M10 x 15.0 4x M12 x 19.0 | 27 | F10 F12 | 4x M10 x 15.0 4x M12 x 19.0 |
| F89-084* | 50.0 14 x 9 |  |  | F10 F14 | 4x M10 x 15.0 4x M16 x 24.0 | 36 | F10 F14 | 4x M10 x 15.0 4x M16 x 24.0 |
| F89-085 | 50.0 14 x 9 |  |  | F12 F16 | 4x M12 x 19.0 4x M20 x 30.0 | 36 | F12 F16 | 4x M12 x 19.0 4x M20 x 30.0 |
| F89-139 | 45.0 14 x 9 |  |  | F14 | 4x M16 x 24.0 |  |  |  |
| F89-140 | 50.0 14 x 9 |  |  | F14 | 4x M16 x 24.0 | 46 | F14 | 4x M16 x 24.0 |
| F89-141 | 50.0 14 x 9 |  |  | F12 F16 | 4x M12 x 19.0 4x M20 x 30.0 | 46 | F12 F16 | 4x M12 x 19.0 4x M20 x 30.0 |
| F89-240 | 70.0 |  | 20 x 12 | F16 F25 | 4x M20 x 30.0 8x M16 x 24.0 | 46 | F16 F25 | 4x M20 x 30.0 8x M16 x 24.0 |

NOTES

F89-084 is identical to F89-085 with F10-F14 flange F89-140 is identical to F89-141 with F14 flange

* F89-084: F10 drilling not in body; please use optional F10 to F14 conversion plate

** Square 14 at 45 degrees

## DIMENSIONS

Pinion connection F89U sizes 002-003	Pinion connection F89U sizes 004-240

G

F

K

Ø F

## TABLE 3B - VALVE CONNECTION KEYSTONE FLANGE

| Model F89-002 | F89U - Keystone metric (mm) F89U - Keystone imperial (in) |  |  |  |  |  |  |  |  |  | Code* |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | F | Bottom of shaft G Key |  | PCD | Mounting holes No x Size x Depth | F | Bottom of shaft G Key |  | PCD | Mounting holes No x Size x Depth |  |
|  | ** |  |  | 44.5 | 4x M6 x 8.0 | *** |  |  | 1¾ | 4x ¼-20 UNC x 0.38 |  |
| F89-003 | 19.0 | 12.7 |  | 44.5 82.5 | 4x M6 x 10.0 4x M10 x 15.0 | ¾ | ½ |  | 1¾ 3¼ | 4x ¼-20 UNC x 0.38 4x ⅜-16 UNC x 0.56 | AAA BAD |
| F89-004 | 20.6 |  | 4.8 x 4.8 | 44.5 82.5 | 4x M6 x 10.0 4x M10 x 15.0 | 13/16 |  | 3/16 x 3/16 | 1¾ 3¼ | 4x ¼-20 UNC x 0.38 4x ⅜-16 UNC x 0.56 | AAA BAC |
| F89-006 | 25.4 |  | 6.4 x 6.4 | 82.5 | 4x M10 x 15.0 | 1 |  | ¼ x ¼ | 3¼ | 4x ⅜-16 UNC x 0.56 | BAD |
| F89-009 | 25.4 |  | 6.4 x 6.4 | 82.5 | 4x M10 x 15.0 | 1 |  | ¼ x ¼ | 3¼ | 4x ⅜-16 UNC x 0.56 | BAD |
| F89-014 | 25.4 |  | 6.4 x 6.4 | 82.5 | 4x M10 x 15.0 | 1 |  | ¼ x ¼ | 3¼ | 4x ⅜-16 UNC x 0.56 | BAD |
| F89-020 | 28.6 |  | 6.4 x 6.4 | 82.5 127.0 | 4x M10 x 15.0 4x M12 x 19.0 | 1⅛ |  | ¼ x ¼ | 3¼ 5 | 4x ⅜-16 UNC x 0.56 4x ½-13 UNC x 0.63 | BAD CAF |
| F89-032 | 28.6 |  | 6.4 x 6.4 | 82.5 127.0 | 4x M10 x 15.0 4x M12 x 19.0 | 1⅛ |  | ¼ x ¼ | 3¼ 5 | 4x ⅜-16 UNC x 0.56 4x ½-13 UNC x 0.63 | BAD CAF |
| F89-033 | 34.9 |  | 7.9 x 7.9 | 82.5 127.0 | 4x M10 x 15.0 4x M12 x 19.0 | 1⅜ |  | 5/16 x 5/16 | 3¼ 5 | 4x ⅜-16 UNC x 0.56 4x ½-13 UNC x 0.63 | BAD CAG |
| F89-051 | 28.6 |  | 6.4 x 6.4 | 82.5 127.0 | 4x M10 x 15.0 4x M12 x 19.0 | 1⅛ |  | ¼ x ¼ | 3¼ 5 | 4x ⅜-16 UNC x 0.56 4x ½-13 UNC x 0.63 | BAD CAF |
| F89-052 | 34.9 |  | 7.9 x 7.9 | 82.5 127.0 | 4x M10 x 15.0 4x M12 x 19.0 | 1⅜ |  | 5/16 x 5/16 | 3¼ 5 | 4x ⅜-16 UNC x 0.56 4x ½-13 UNC x 0.63 | BAD CAG |
| F89-085 | 41.3 |  | 9.5 x 9.5 | 127.0 165.0 | 4x M12 x 19.0 4x M20 x 30.0 | 1⅝ |  | ⅜ x ⅜ | 5 6½ | 4x ½-13 UNC x 0.63 4x ¾-10 UNC x 1.00 | CAH DAH |
| F89-086 | 47.6 |  | 12.7 x 9.5 | 127.0 165.0 | 4x M12 x 19.0 4x M20 x 30.0 | 1⅞ |  | ½ x ⅜ | 5 6½ | 4x ½-13 UNC x 0.63 4x ¾-10 UNC x 1.00 | CAJ DAJ |
| F89-140 | 57.2 |  | 12.7 x 9.5 | 127.0 165.0 | 4x M12 x 19.0 4x M20 x 30.0 | 2¼ |  | ½ x ⅜ | 5 6½ | 4x ½-13 UNC x 0.63 4x ¾-10 UNC x 1.00 | CAK DAK |
| F89-240 | 57.2 |  | 12.7 x 9.5 | 165.0 | 4x M20 x 30.0 | 2¼ |  | ½ x ⅜ | 6½ | 4x ¾-10 UNC x 1.00 | DAK |

NOTES

F89-033 is identical to F89-032 with larger bore F89-051 is identical to F89-052 with smaller bore F89-084 is identical to F89-085 with smaller bore F89-086 is identical to F89-085 with larger bore

* Keystone mounting compatibility code

** Square 14 at 45 degrees

*** Square 0.55 at 45 degrees

## TOP MOUNT DRILLING

The top mount drilling is available with metric or imperial threading. The dimensions of the hole pattern are identical.

30 (1.18) 41.1 (1.62)

H

J

93.5 (3.68)

130.0 (5.12)

H

30 (1.18) 41.1 (1.62)

J

80 (3.15)

93.5 (3.68)

H

30 (1.18)	41.1 (1.62)

J

80 (3.15)

93.5 (3.68)

Top mounting drilling sizes 002 - 020	Top mounting drilling sizes 032 - 052	Top mounting drilling sizes 084 - 240

NOTES

- For model 002/003 the Keystone drilling pattern (93.5x41.1mm) exceeds the body dimensions. Please add Keystone mounting plate option (item 11425095).

- Metric threaded versions have a bolt threading of M5x1.0 x 10.0 mm deep.

- Imperial threaded versions have a bolt threading of 10-32 UNF x 0.28 inch deep.

## NAMUR VDI/VDE 3845 MOUNTING

Full adoption to the VDI/VDE 3845 standard can be achieved with the introduction of a male insert into the female shaft.

4.0

(0.16)

(0.79) (0.16)

20.0

4.0

Ø 16.0

(0.63)

M6 x 0.47

11.0 (0.43) A/F

## AIR CONNECTION

The actuator is controlled by applying compressed air to the ¼” BSP/NPT ports (½” BSP/NPT for Model F89-240), or with a Namur solenoid valve.

B port

¼" BSP/NPT

A port

12 (0.47)

32 (1.26)

¼" BSP/NPT 24 (0.95)

A port

(0.79)

20

45 (1.77)

½" BSP/NPT

40 (1.58)

B port

16 (0.63)

B port

22.5 (0.89)

A port

32 (1.26)

16 (0.63)

12 (0.47)

24 (0.95)

Air connection sizes 002 - 052	Air connection sizes 085 - 140	Air connection size 240

NOTES

- Metric threaded versions have a bolt threading of M5x1.0 x 10.0 mm deep.

- Imperial threaded versions have a bolt threading of 10-32 UNF x 0.28 inch deep.

- F89D has BSP air connections only

## ACTUATOR PISTON DISPLACEMENT

Piston displacement is the total volume of pressurized air after the actuator has completed its stroke.

## TABLE 4 - ACTUATOR VOLUME

NOTES

Air consumption calculation: volume in table represents actual free air volume in either open or close direction.

Air consumption will vary depending on supply pressure. To determine air consumption per minute

|  |  | Opening |  |  | Closing |  | use the following formula: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | litres |  | cu.in | litres |  | cu.in |  |  |  |  |
| F89-002 | 0.11 |  | 6.7 | 0.09 |  | 5.5 | Double acting (nL/min): |  |  |  |
| F89-003 | 0.17 |  | 10.4 | 0.14 |  | 8.5 | Open + Supply |  |  |  |
| F89-004 | 0.25 | 15.3 |  | 0.21 | 12.8 |  | Close volume (l) |  | air pressure + 1 | Cycles/ |
| F89-006 | 0.36 | 21.8 |  | 0.29 | 17.7 |  | 1 |  | 1 | Min |
| F89-009 | 0.57 | 34.9 |  | 0.48 | 29.3 |  | Double acting (SCFM): |  |  |  |

F89-014	0.90	54.9

F89-020	1.37	83.8

F89-032/033	2.10	128.2

F89-051/052	3.10	189.2

F89-084/085/086	5.09	310.6

F89-139/140/141	8.92	544.3

F89-240	15.40	939.8

0.73	44.5

1.08	65.9

1.66	101.3

2.63	160.5

3.87	236.2

6.81	415.6

12.63	770.7

Cycles/ Min

Close volume (in3)

Open +

Supply

172) 8

air pressure + 14.7

14.7

TABLE 5 - ACTUATOR CYCLING TIME (s)

| Model | DA |  |  |  |  |  |  | SR |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Travel Opening | time Closing |  | Total time Opening | Closing | Travel time Opening Closing |  | Total time Opening Closing |  |  |
| F89-002 | 0.1 | 0.0 | 0.1 |  | 0.0 |  |  |  |  |  |
| F89-003 | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 |
| F89-004 | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 |
| F89-006 | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 |
| F89-009 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 |
| F89-014 | 0.3 | 0.2 | 0.3 |  | 0.3 | 0.4 | 0.2 |  | 0.5 | 0.2 |
| F89-020 | 0.4 | 0.3 | 0.5 |  | 0.4 | 0.9 | 0.3 |  | 1.0 | 0.4 |
| F89-032/033 | 0.5 | 0.5 | 0.7 |  | 0.6 | 1.0 | 0.5 |  | 1.2 | 0.7 |
| F89-051/052 | 0.8 | 0.7 | 1.1 |  | 0.9 | 1.2 | 0.7 |  | 1.5 | 0.9 |
| F89-084/085/086 | 0.8 | 0.8 | 1.8 |  | 1.7 | 1.9 | 0.6 |  | 3.0 | 1.1 |
| F89-139/140/141 | 1.4 | 1.5 | 3.1 |  | 2.9 | 3.2 | 1.1 |  | 5.0 | 1.8 |
| F89-240 | 2.9 | 3.4 | 6.5 |  | 6.0 | 6.1 | 4.1 |  | 9.7 | 6.9 |

NOTES

- The actuator stroke time consist of the time required to build up pressure in the actuator and consequently move the pistons and valve (=travel time). The sum of these values is the total cycling time.

- The actuator stroke time varies with the supplied air pressure, solenoid valve, and required valve torque, and are for indication only.

- Speed reduction on inlet or exhaust ports will improve actuator endurance and are required to meet the lifetime as per EN15714-3 standard.

- Indicated stroke times above are based on a bare actuator using 5.5 bar (80 psi) air pressure and a solenoid valve with Cv of 1300 l/m (46 CFM).

## TABLE 6 - ACTUATOR WEIGHT

|  |  | DA |  |  | SR |  |
| --- | --- | --- | --- | --- | --- | --- |
| Model | kg |  | lbs | kg |  | lbs |
| F89-002 | 1.0 |  | 2.2 | - |  | - |
| F89-003 | 1.4 |  | 3.1 | 1.7 |  | 3.7 |
| F89-004 | 2.1 |  | 4.6 | 2.6 |  | 5.7 |
| F89-006 | 2.9 |  | 6.4 | 3.6 |  | 7.9 |
| F89-009 | 3.7 |  | 8.2 | 4.9 |  | 10.8 |
| F89-014 | 5.3 |  | 11.7 | 7.3 |  | 16.1 |
| F89-020 | 7.9 |  | 17.4 | 11.0 |  | 24.3 |
| F89-032/033 | 12.1 |  | 26.7 | 16.7 |  | 36.8 |
| F89-051/052 | 18.3 |  | 40.3 | 24.9 |  | 54.9 |
| F89-084/085/086 | 27.8 |  | 61.3 | 39.7 |  | 87.5 |
| F89-139/140/141 | 45.8 |  | 101.0 | 69.5 |  | 153.2 |
| F89-240 | 77.5 |  | 170.9 | 112.4 |  | 247.8 |

MATERIALS OF CONSTRUCTION

22	15	20	8	7	9	3	1	25	14	3	6

18

21

23

19

12

16	5

10

4	2

11

17

13

24

## TABLE 7 - MATERIALS OF CONSTRUCTION

| No. | Item | Material | US material std | BS material std | DIN material std | Finish |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Body | Extruded aluminium ASTM B221 type 6063T6 | ASTM B221 | BS 1474 6063 | DIN 3.33206.51 | Anodized 5-8 microns + ESPC 60-80 microns |
| 2 | Pinion | Hot rolled carbon steel bar ASTM A108 grade 1045 | A108 | BS 970 080M40 | C40 | Zink-Nickel plated 8-12 microns |
| 3 | Piston | Die cast aluminium alloy ASTM B85 type A380 /BS 1490 grade LM24 | ASTM B85 | BS 1490 | DIN 1725-2300 or 226 | Anodized |
| 4 | End cap | Die cast aluminium alloy ASTM B85 type A380/BS 1490 grade LM24 | ASTM B85 | BS 1490 | DIN 1725-2300 or 226 | ESPC 60-80 microns |
| 5 | Cam | Cast grade SAE 1045/C45 / EN8 |  |  |  | Blackodised |
| 6 | Spring | Spring steel as per ASTM A401 | ASTM A401 | BS 5216 HS3 | DIN 17223 Pti | Epoxy coated 30-40 microns |
| 7 | Spring retainer | Carbon steel |  |  |  | Zinc plated |
| 8 | Spring cup | Die cast aluminium alloy ASTM B85 type A380 /BS 1490 grade LM24 (PA66 up to model 052) | ASTM B85 | BS 1490 | DIN1725-2300 or 226 | Anodized |
| 9 | Piston guide | Zytel 101F NC010 |  |  |  | Natural |
| 10 | Top bearing | PAR (1) + 25% glass filled |  |  |  | Natural |
| 11 | Bottom bearing | PAR (1) + 25% glass filled |  |  |  | Natural |
| 12 | Top thrust washer | PA66 (2) |  |  |  | Natural |
| 13 | Bottom thrust washer | PA66 (2) |  |  |  | Natural |
| 14 | Travel stop washer | SS (3) ISO 3506 A2-70 grade |  |  |  | Natural |
| 15 | End cap washer (spring washer) | SS (3) ISO 3506 A2-70 grade |  |  |  | Natural |
| 16 | Top O-ring (pinion) | NBR shore 70 A |  |  |  | Natural |
| 17 | Bottom O-ring (pinion) | NBR shore 70 A |  |  |  | Natural |
| 18 | O-ring (piston) | NBR shore 70 A |  |  |  | Natural |
| 19 | O-ring (travel stop) | NBR shore 70 A |  |  |  | Natural |
| 20 | Gasket (end cap) | NBR shore 70 A |  |  |  | Natural |
| 21 | Bolt - travel stop | SS (3) ISO 3506 A2-70 grade |  |  |  | Natural |
| 22 | Bolt - end cap | SS (3) ISO 3506 A2-70 grade |  |  |  | Natural |
| 23 | Nut - travel stop | SS (3) ISO 3506 A2-70 grade |  |  |  | Natural |
| 24 | Circlip (bottom) | Carbon steel |  |  |  | Zink-Nickel plated |
| 25 | Position indicator | ABS plastic |  |  |  | Natural |

1. POM Acetal Resin	2. Polyamide grade 66	3. Stainless steel

## TORQUE OUTPUT

Double acting actuator

For sizing of double acting actuators use the following table and select the actuator

which will provide nearest torque output above the anticipated torque of the valve and required safety factor.

| F89-002 | 11 | 15 | 18 | 20 | 22 | 25 | 30 |  | F89-002 100 | 134 | 167 | 184 | 201 | 234 | 277 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| F89-003 | 17 | 22 | 28 | 31 | 33 | 39 | 46 |  | F89-003 147 | 197 | 246 | 270 | 295 | 344 | 408 |
| F89-004 | 25 | 34 | 42 | 46 | 50 | 59 | 70 |  | F89-004 223 | 297 | 372 | 409 | 446 | 521 | 617 |
| F89-006 | 36 | 48 | 60 | 66 | 72 | 84 | 100 |  | F89-006 320 | 427 | 534 | 587 | 641 | 747 | 886 |
| F89-009 | 58 | 77 | 96 | 106 | 116 | 135 | 160 |  | F89-009 512 | 683 | 853 | 938 | 1024 | 1194 | 1416 |
| F89-014 | 90 | 121 | 151 | 166 | 181 | 211 | 250 |  | F89-014 801 | 1068 | 1334 | 1468 | 1601 | 1868 | 2215 |
| F89-020 | 132 | 177 | 221 | 243 | 265 | 309 | 366 |  | F89-020 1173 | 1563 | 1954 | 2150 | 2345 | 2736 | 3244 |
| F89-032/033 | 208 | 277 | 346 | 381 | 416 | 485 | 575 |  | F89-032/033 1841 | 2455 | 3068 | 3375 | 3682 | 4295 | 5093 |
| F89-051/052 | 315 | 420 | 525 | 577 | 630 | 735 | 871 |  | F89-051/052 2789 | 3718 | 4648 | 5112 | 5577 | 6507 | 7715 |
| F89-084/085/086 | 525 | 701 | 876 | 963 | 1051 | 1226 | 1454 |  | F89-084/085 4652 | 6203 | 7754 | 8529 | 9304 | 10855 | 12871 |
| F89-139/140/141 | 913 | 1218 | 1522 | 1674 | 1826 | 2131 | 2527 |  | F89-140/141 7749 | 10332 | 12915 | 14206 | 15497 | 18080 | 21438 |
| F89-240 | 1508 | 2011 | 2514 | 2765 | 3017 | 3520 | 4173 |  | F89-240 13357 | 17810 | 22262 | 24489 | 26715 | 31167 | 36955 |

TABLE 8 - DA TORQUE (Nm)

| Model | Air pressure (bar) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3 | 4 | 5 | 5.5 | 6 | 7 | 8.3 |

Spring return actuator

Sizing of spring return actuators is more complex. First you need to determine

the desired 'failure mode' (fail open or fail closed). Secondly you need to determine

the critical torque points for the subject valve using the table below.

## TABLE 9 - DA TORQUE (in·lb)

| Model | Air pressure (psi) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 40 | 60 | 70 | 80 | 90 | 100 | 120 |

Butterfly valves 'fail closed'	Butterfly valves 'fail open'

Start of air torque

End of spring torque

Start of spring torque

End of air torque

Ball valves 'fail closed'	Ball valves 'fail open'

Start of air (unseating) torque	Start of spring (unseating) torque

End of air (full open) torque	End of spring (full open) torque

Start of spring (breakout from open) torque	Start of air (breakout from open) torque End of spring (re-seating) torque	End of air (re-seating) torque

## TABLE 10 - SR TORQUE (Nm)

| Number Model of springs F89-003 4 5 6 7 8 9 10 11 12 | Air pressure (bar) Spring torque |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3 4 5 5.5 6 7 8.3 AST AET AST AET AST AET AST AET AST AET AST AET AST AET SST SET |  |  |  |  |  |  |  |
|  | 11 8 9 6 8 3 7 1 | 16 13 15 11 14 9 12 7 11 4 9 2 | 22 19 21 17 19 14 18 12 16 10 15 8 13 6 12 3 | 25 22 23 19 22 17 20 15 19 13 17 11 16 8 15 6 13 4 | 28 24 26 22 25 20 23 18 22 16 20 13 19 11 17 9 16 7 | 33 30 32 28 30 26 29 23 27 21 26 19 24 17 23 14 21 12 | 40 37 39 35 37 33 36 31 34 28 33 26 32 24 30 22 29 19 | 9 6 11 7 13 9 16 10 18 12 20 13 22 15 24 16 27 17 |
| F89-004 4 5 6 7 8 9 10 11 12 | 17 12 15 9 12 6 10 3 | 25 21 23 17 21 14 19 11 17 8 14 4 | 33 29 31 26 29 23 27 19 25 16 23 13 21 10 19 6 | 38 33 36 30 33 27 31 23 29 20 27 17 25 14 23 11 21 7 | 42 37 40 34 38 31 35 28 33 24 31 21 29 18 27 15 25 11 | 50 46 48 43 46 39 44 36 42 33 40 30 37 26 35 23 33 20 | 61 57 59 53 57 50 55 47 53 44 50 41 48 37 46 34 44 31 | 13 9 16 11 19 13 23 15 26 17 29 19 32 21 36 23 39 26 |
| F89-006 4 5 6 7 8 9 10 11 12 | 24 13 21 7 18 2 | 36 25 33 19 30 14 27 8 24 2 | 48 37 45 31 42 26 39 20 36 14 33 9 30 3 | 54 43 51 37 48 32 45 26 42 20 39 15 36 9 33 3 | 60 49 57 43 54 38 51 32 48 26 45 21 42 15 39 9 37 4 | 72 61 69 55 66 50 63 44 60 38 57 33 54 27 51 21 49 16 | 88 77 85 71 82 65 79 60 76 54 73 48 70 43 67 37 64 31 | 23 12 29 15 34 18 40 21 46 24 51 27 57 30 63 33 69 36 |
| F89-009 4 5 6 7 8 9 10 11 12 | 38 29 33 21 29 14 24 7 | 58 48 53 41 48 33 43 26 38 19 33 11 | 77 67 72 60 67 53 62 45 57 38 53 31 48 23 43 16 | 87 77 82 70 77 62 72 55 67 48 62 40 57 33 52 26 48 18 | 96 86 91 79 86 72 82 65 77 57 72 50 67 43 62 35 57 28 | 115 106 111 98 106 91 101 84 96 77 91 69 86 62 81 55 77 47 | 140 131 136 123 131 116 126 109 121 102 116 94 111 87 106 80 102 72 | 29 19 36 24 44 29 51 34 58 39 66 44 73 49 80 53 88 58 |
| F89-014 4 5 6 7 8 9 10 11 12 | 60 46 53 35 45 23 38 12 | 91 76 83 65 75 53 68 42 60 31 53 20 | 121 106 113 95 106 84 98 72 91 61 83 50 76 39 68 28 | 136 121 128 110 121 99 113 88 106 76 98 65 91 54 83 43 76 32 | 151 136 143 125 136 114 128 103 121 91 113 80 106 69 98 58 91 47 | 181 166 173 155 166 144 158 133 151 122 143 110 136 99 128 88 121 77 | 220 205 213 194 205 183 198 172 190 161 183 150 175 138 168 127 160 116 | 45 30 56 38 67 45 78 53 89 60 101 68 112 75 123 83 134 90 |
| F89-020 4 5 6 7 8 9 10 11 12 | 86 62 74 45 62 27 51 10 | 130 107 118 89 107 72 95 54 83 37 72 19 | 174 151 162 133 151 116 139 98 127 81 116 63 104 46 92 28 | 196 173 184 155 173 138 161 120 149 103 138 85 126 68 114 50 103 33 | 218 195 206 177 195 160 183 142 171 125 160 107 148 90 136 72 125 55 | 262 239 251 221 239 204 227 186 216 169 204 151 192 134 181 116 169 99 | 320 296 308 279 296 261 285 244 273 226 261 209 250 191 238 174 226 156 | 70 47 88 58 105 70 123 82 140 93 158 105 175 117 193 128 210 140 |

TABLE 10 - SR TORQUE (Nm) continued

| Number Model of springs F89- 4 032/033 5 6 7 8 9 10 11 12 | Air pressure (bar) Spring torque |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3 4 5 5.5 6 7 8.3 AST AET AST AET AST AET AST AET AST AET AST AET AST AET SST SET |  |  |  |  |  |  |  |
|  | 134 96 115 69 96 41 78 13 | 203 166 184 138 166 110 147 82 129 54 110 26 | 272 235 254 207 235 179 216 151 198 124 179 96 161 68 142 40 | 307 270 288 242 270 214 251 186 232 158 214 130 195 102 177 75 158 47 | 341 304 323 276 304 249 286 221 267 193 249 165 230 137 211 109 193 81 | 411 374 392 346 374 318 355 290 336 262 318 234 299 206 281 178 262 151 | 501 464 482 436 464 408 445 380 426 352 408 324 389 296 371 269 352 241 | 111 74 139 93 167 111 195 130 223 149 251 167 279 186 307 204 334 223 |
| F89- 4 051/052 5 6 7 8 9 10 11 12 | 195 135 165 90 135 45 105 1 | 300 240 270 195 240 150 210 105 180 61 150 16 | 405 345 375 300 345 255 315 210 285 166 255 121 225 76 195 31 | 457 398 428 353 398 308 368 263 338 218 308 173 278 128 248 83 218 38 | 510 450 480 405 450 360 420 315 390 270 360 226 330 181 300 136 270 91 | 615 555 585 510 555 465 525 420 495 375 465 331 435 286 405 241 375 196 | 751 691 721 647 691 602 662 557 632 512 602 467 572 422 542 377 512 332 | 180 120 225 150 269 180 314 210 359 240 404 269 449 299 494 329 539 359 |
| F89- 4 084/085/ 5 086 6 7 8 9 10 11 12 | 329 231 280 157 231 83 181 10 | 504 406 455 332 406 258 356 185 307 111 258 37 | 679 581 630 507 581 433 531 360 482 286 433 212 384 139 335 65 | 767 669 718 595 669 521 619 448 570 374 521 300 472 227 423 153 374 80 | 855 757 806 683 757 609 707 536 658 462 609 388 560 315 511 241 462 168 | 1030 932 981 858 932 784 882 711 833 637 784 563 735 490 686 416 637 343 | 1257 1159 1208 1085 1159 1011 1109 938 1060 864 1011 790 962 717 913 643 864 570 | 294 196 368 245 442 294 515 344 589 393 663 442 736 491 810 540 883 589 |
| F89-139/ 4 140/141 5 6 7 8 9 10 11 12 | 548 384 466 262 384 139 303 16 | 840 676 758 554 676 431 595 308 513 186 431 63 | 1131 967 1049 845 967 722 886 599 804 477 722 354 640 231 558 109 | 1277 1113 1195 991 1113 868 1032 745 950 623 868 500 786 377 704 255 623 132 | 1423 1259 1341 1137 1259 1014 1178 891 1096 769 1014 646 932 523 850 401 769 278 | 1714 1550 1632 1428 1550 1305 1469 1182 1387 1060 1305 937 1223 814 1141 692 1060 569 | 2094 1930 2012 1808 1930 1685 1849 1562 1767 1440 1685 1317 1603 1194 1521 1072 1440 949 | 491 327 613 409 736 491 859 572 981 654 1104 736 1227 818 1349 900 1472 981 |
| F89-240 4 5 6 7 8 9 10 11 12 | 954 676 815 469 676 261 538 53 | 1457 1179 1318 972 1179 764 1041 556 902 348 764 140 | 1960 1682 1821 1475 1682 1267 1544 1059 1405 851 1267 643 1128 435 990 227 | 2211 1933 2072 1726 1933 1518 1795 1310 1656 1102 1518 894 1379 686 1241 478 1102 270 | 2462 2184 2323 1977 2184 1769 2046 1561 1907 1353 1769 1145 1630 937 1492 729 1353 521 | 2965 2687 2826 2480 2687 2272 2549 2064 2410 1856 2272 1648 2133 1440 1995 1232 1856 1024 | 3619 3341 3480 3134 3341 2926 3203 2718 3064 2510 2926 2302 2787 2094 2649 1886 2510 1678 | 832 554 1039 693 1247 832 1455 970 1663 1109 1871 1247 2079 1386 2287 1524 2495 1663 |

TABLE 11 - SR TORQUE (in·lb)

| Number Model of springs F89-003 4 5 6 7 8 9 10 11 12 | Air pressure (psi) Spring torque |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 40 60 70 80 90 100 120 AST AET AST AET AST AET AST AET AST AET AST AET AST AET SST SET |  |  |  |  |  |  |  |
|  | 97 71 80 53 70 30 58 10 | 142 115 133 97 120 79 107 59 94 39 81 20 | 195 168 186 151 169 128 156 108 143 89 130 69 117 49 105 30 | 221 195 204 168 193 153 180 133 168 113 155 94 142 74 129 54 116 35 | 248 213 230 195 218 177 205 157 192 138 179 118 167 99 154 79 141 59 | 292 266 283 248 267 226 254 207 241 187 229 167 216 148 203 128 190 108 | 354 328 345 310 331 290 318 270 305 251 292 231 280 212 267 192 254 172 | 80 53 97 62 118 77 137 90 157 103 177 116 196 128 216 141 236 154 |
| F89-004 4 5 6 7 8 9 10 11 12 | 151 106 133 80 110 51 91 22 | 221 186 204 151 184 125 165 97 146 68 127 39 | 292 257 275 230 259 200 240 171 221 142 202 113 183 85 164 56 | 337 292 319 266 296 237 277 208 258 179 239 151 220 122 201 93 182 65 | 372 328 354 301 333 274 314 245 295 217 276 188 257 159 238 130 220 102 | 443 407 425 381 407 348 388 320 369 291 351 262 332 233 313 205 294 176 | 540 505 523 469 504 445 485 416 466 388 447 359 428 330 409 301 391 273 | 115 80 142 97 172 113 201 132 230 151 258 170 287 189 316 208 344 227 |
| F89-006 4 5 6 7 8 9 10 11 12 | 214 117 188 66 162 15 | 320 223 294 172 268 122 242 71 215 21 | 426 329 400 278 374 228 348 177 322 127 295 76 269 26 | 479 382 453 332 427 281 401 230 375 180 348 129 322 79 296 28 | 533 435 506 385 480 334 454 284 428 233 402 183 375 132 349 82 323 31 | 639 541 613 491 586 440 560 390 534 339 508 289 482 238 455 188 429 137 | 777 679 751 629 724 578 698 528 672 477 646 427 620 376 594 326 567 275 | 202 105 253 131 303 157 354 183 404 210 455 236 505 262 556 288 606 314 |
| F89-009 4 5 6 7 8 9 10 11 12 | 337 257 292 186 254 124 210 60 | 514 425 469 363 424 295 381 230 338 166 295 101 | 682 593 638 531 595 466 552 401 509 336 466 272 423 207 380 143 | 771 682 726 620 680 551 637 486 594 422 551 357 508 293 465 228 422 163 | 850 762 806 700 765 636 722 572 679 507 636 443 593 378 550 313 507 249 | 1019 939 983 868 936 807 893 742 850 678 807 613 764 549 721 484 678 419 | 1240 1160 1204 1089 1158 1029 1115 964 1072 900 1029 835 986 770 943 706 900 641 | 257 168 319 213 388 258 452 301 517 344 581 388 646 431 710 474 775 517 |
| F89-014 4 5 6 7 8 9 10 11 12 | 531 407 469 310 402 207 335 108 | 806 673 735 576 669 474 602 375 536 276 469 177 | 1072 939 1001 841 936 741 869 642 803 543 736 444 670 345 603 246 | 1204 1072 1134 974 1069 874 1002 775 936 676 870 577 803 478 737 379 670 280 | 1337 1204 1266 1107 1202 1008 1136 909 1069 810 1003 711 937 612 870 513 804 414 | 1603 1470 1532 1373 1469 1274 1403 1175 1336 1076 1270 978 1203 879 1137 780 1070 681 | 1948 1816 1886 1718 1816 1621 1750 1522 1683 1423 1617 1324 1550 1226 1484 1127 1417 1028 | 399 266 496 337 594 399 693 465 792 532 891 598 990 665 1089 731 1188 798 |
| F89-020 4 5 6 7 8 9 10 11 12 | 762 549 655 399 553 243 449 88 | 1151 948 1045 788 943 633 840 478 737 323 633 168 | 1541 1337 1435 1178 1334 1024 1231 869 1128 714 1024 559 921 404 818 249 | 1736 1532 1630 1373 1530 1220 1426 1065 1323 910 1220 755 1116 600 1013 445 910 290 | 1931 1727 1824 1568 1725 1415 1622 1260 1518 1105 1415 950 1312 795 1208 640 1105 485 | 2320 2117 2223 1957 2116 1806 2013 1651 1909 1496 1806 1341 1703 1186 1599 1031 1496 876 | 2834 2622 2728 2471 2624 2314 2521 2159 2418 2004 2314 1849 2211 1694 2107 1539 2004 1384 | 620 416 779 514 930 620 1085 723 1240 827 1395 930 1550 1033 1705 1137 1860 1240 |

TABLE 11 - SR TORQUE (in·lb) continued

| Number Model of springs F89- 4 032/033 5 6 7 8 9 10 11 12 | Air pressure (psi) Spring torque |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 40 60 70 80 90 100 120 AST AET AST AET AST AET AST AET AST AET AST AET AST AET SST SET |  |  |  |  |  |  |  |
|  | 1187 850 1019 611 854 360 689 113 | 1798 1470 1630 1222 1467 974 1303 727 1138 480 974 233 | 2409 2081 2250 1833 2081 1587 1916 1341 1752 1094 1587 847 1423 600 1258 353 | 2719 2391 2551 2143 2388 1894 2223 1647 2059 1401 1894 1154 1730 907 1565 660 1401 413 | 3020 2692 2861 2444 2695 2201 2530 1954 2366 1707 2201 1461 2037 1214 1872 967 1707 720 | 3640 3312 3472 3064 3308 2815 3144 2568 2979 2321 2815 2074 2650 1828 2486 1581 2321 1334 | 4437 4109 4269 3861 4106 3612 3942 3366 3777 3119 3612 2872 3448 2625 3283 2378 3119 2132 | 983 655 1231 824 1481 987 1728 1152 1974 1316 2221 1481 2468 1645 2715 1810 2962 1974 |
| F89- 4 051/052 5 6 7 8 9 10 11 12 | 1727 1196 1461 797 1198 402 933 5 | 2657 2126 2391 1727 2127 1332 1862 934 1597 536 1332 139 | 3587 3056 3321 2657 3057 2261 2792 1864 2526 1466 2261 1068 1996 670 1731 273 | 4047 3525 3791 3126 3522 2726 3256 2328 2991 1931 2726 1533 2461 1135 2196 737 1931 340 | 4517 3985 4251 3587 3986 3191 3721 2793 3456 2395 3191 1998 2926 1600 2661 1202 2395 805 | 5447 4915 5181 4517 4916 4120 4651 3723 4386 3325 4120 2927 3855 2530 3590 2132 3325 1734 | 6651 6120 6386 5730 6124 5329 5859 4931 5594 4533 5329 4136 5064 3738 4799 3340 4533 2942 | 1594 1063 1993 1328 2386 1591 2784 1856 3182 2121 3580 2386 3977 2652 4375 2917 4773 3182 |
| F89- 4 084/085/ 5 086 6 7 8 9 10 11 12 | 2916 2048 2482 1393 2048 738 | 4467 3599 4033 2944 3599 2288 3156 1642 2722 986 | 6018 5150 5584 4494 5150 3839 4707 3192 4273 2537 3839 1882 3405 1235 2971 580 | 6793 5925 6359 5270 5925 4614 5482 3968 5048 3312 4614 2657 4180 2010 3746 1355 3312 709 | 7568 6700 7134 6045 6700 5390 6258 4743 5824 4088 5390 3432 4956 2786 4522 2130 4088 1484 | 9119 8251 8685 7596 8251 6940 7808 6294 7374 5638 6940 4983 6506 4337 6072 3681 5638 3035 | 11135 10267 10701 9612 10267 8956 9824 8310 9390 7654 8956 6999 8522 6352 8088 5697 7654 5051 | 2604 1736 3259 2170 3915 2604 4561 3047 5217 3481 5872 3915 6518 4349 7174 4783 7820 5217 |
| F89-139/ 4 140/141 5 6 7 8 9 10 11 12 | 4853 3400 4126 2320 3400 1230 | 7436 5983 6709 4903 5983 3813 5266 2724 4539 1643 | 10018 8566 9292 7485 8566 6396 7849 5307 7122 4226 6396 3137 5670 2047 4944 967 | 11310 9857 10584 8777 9857 7688 9140 6598 8414 5518 7688 4428 6961 3339 6235 2258 5518 1169 | 12601 11149 11875 10068 11149 8979 10431 7890 9705 6809 8979 5720 8253 4630 7527 3550 6809 2461 | 15184 13732 14458 12651 13732 11562 13014 10473 12288 9392 11562 8303 10836 7213 10109 6133 9392 5043 | 18542 17090 17816 16009 17090 14920 16372 13830 15646 12750 14920 11660 14193 10571 13467 9491 12750 8401 | 4349 2896 5429 3622 6518 4349 7608 5066 8688 5792 9778 6518 10867 7245 11948 7971 13037 8688 |
| F89-240 4 5 6 7 8 9 10 11 12 | 8451 5989 7220 4155 5989 2313 | 12903 10441 11672 8608 10441 6766 9219 4923 7988 3081 | 17356 14894 16125 13060 14894 11218 13671 9376 12440 7534 11218 5692 9987 3849 8765 2007 | 19582 17120 18351 15286 17120 13444 15898 11602 14667 9760 13444 7918 12213 6076 10991 4233 9760 2391 | 21808 19346 20577 17513 19346 15671 18124 13828 16893 11986 15671 10144 14439 8302 13217 6460 11986 4618 | 26261 23798 25030 21965 23798 20123 22576 18281 21345 16439 20123 14596 18892 12754 17670 10912 16439 9070 | 32049 29587 30818 27753 29587 25911 28364 24069 27133 22227 25911 20385 24680 18543 23458 16700 22227 14858 | 7369 4907 9202 6138 11044 7369 12886 8591 14729 9822 16571 11044 18413 12275 20255 13497 22097 14729 |

ORDERING GUIDE

Example:	89E	020	03	08	N14	N	2	M	00	M10	D25

Figure number

89D	ISO 5211 flange and shaft

89E	ISO flange and Keystone shaft 89U	Keystone flange and shaft Model/Size

002	002	020	020	085	085

003	003	032	032	086	086

004	004	033	033	139	139

006	006	051	051	140	140

009	009	052	052	141	141

014	014	084	084	240	240

Action

01	DA

- SR FC CW (std)

- SR FC CCW

Spring rating

- 4 springs	08	8 springs	12	12 springs

- 5 springs	09	9 springs	XX	not applicable

- 6 springs	10	10 springs

- 7 springs	11	11 springs

Air connection

N14	¼" NPT	P14	¼" BSPP

N12	½" NPT (F89-240 only)	P12	½" BSPP (89-240 only)

Temperature range

H	High temp (FKM)

N	Standard (NBR)

L	Low temp

Travel stops

- Dual shaft (std)

- Single stroke limiter (endcap)

- Double stroke limiter (endcap)

Flange threading M	Metric

U	Imperial

Variant

00	Standard

A4	A4 SS bolts

Valve flange*

F03    PCD 36 mm (ISO 5211)	M05     F03 + F05 (ISO 5211)	U1C PCD 1.75" (Keystone 45 degrees) F04    PCD 42 mm (ISO 5211)	M07     F05 + F07 (ISO 5211)	U34 PCD 3.25" (Keystone 45 degrees) F05    PCD 50 mm (ISO 5211)	M10   F07 + F10 + F12 (ISO 5211)   U50  PCD 5.00" (Keystone 45 degrees) F07    PCD 70 mm (ISO 5211)	M11    F07+F10+F12 (ISO5211)	U68 PCD 6.50" (Keystone 45 degrees) F10   PCD 102 mm (ISO 5211)	M12 F10 + F12 (ISO 5211)

F12   PCD 125 mm (ISO 5211)	M14     F10 + F14 (ISO 5211)	C34 PCD 1.75 + 3.25" (Keystone 45 degrees) F14   PCD 140 mm (ISO 5211)	M16     F12 + F16 (ISO 5211)	C50 PCD 3.25 + 5.00" (Keystone 45 degrees) F16   PCD 165 mm (ISO 5211)		C68 PCD 5.00 + 6.50" (Keystone 45 degrees)

Shaft*

S11	Star 11	D12	E1 - DD12 x 8	P06	DD ⅜" x ¼" (9.53 x 6.35 mm)

S14	Star 14	D16	E2 - DD16 x 11	P09	DD 9/16" x ⅜" (14.29 x 9.53 mm)

S17	Star 17	D20	E3 - DD20 x 14	P0A	DD ⅝" x 7/16" (15.88 x 11.1 mm)

S22	Star 22	D25	E4 - DD25 x 18	P0C	DD ¾" x ½" (19.05 x 12.7 mm)

S27	Star 27	D30	E5 - DD30 x 22	P0E	DD ⅞" x ⅝" (22.2 x 15.88 mm)

S36	Star 36	M35	E6 - 35K10	U0D	Dia 13/16"; K 3/16 x 3/16" (20.6K4.78 mm)

S46	Star 46	M40	E7 - 40K12	U10	Dia 1"; K1¼x¼" (25.4K6.35 mm)

S55	Star 55	M44	E8 - 44K12	U12	Dia 1⅛"; K¼x¼" (28.8K6.35 mm)

S75	Star 75	M50	E9 - 50K14	U16	Dia 1⅜"; K 5/16 x 5/16" (34.9K7.94 mm)

M60	E0 - 60K18	U1A	Dia 1⅝"; K ⅜ x ⅜" (41.3K9.53 mm)

M70	EA - 70K20	U1E	Dia 1⅞"; K ½ x ⅜" (47.6K12.7 mm)

M80	EB - 80K22	U24	Dia 2¼; K ½ x ⅜" (57.2K12.7 mm)

M90	EC - 90K25	U26	Dia 2⅜"; K ⅝" (63.3K15.9 mm)

MA0	ED - 100K28	U2C	Dia 2¾"; K ⅝" (69.9K15.9 mm)

MS0	Bore 30 x K8 (Keystone)	U38	Dia 3½"; K ⅞" (88.9K22.23 mm)

* Please consult technical pages for the specific flange and shaft details per model.

Neither Emerson, Emerson Automation Solutions, nor any of their affiliated entities assumes responsibility for the selection, use or maintenance of any product. Responsibility for proper selection, use, and maintenance of any product remains solely with the purchaser and end user.

Keystone is a mark owned by one of the companies in the Emerson Automation Solutions business unit of Emerson Electric Co. Emerson Automation Solutions, Emerson and the Emerson logo are trademarks and service marks of Emerson Electric Co. All other marks are the property of their respective owners.

The contents of this publication are presented for informational purposes only, and while every effort has been made to ensure their accuracy, they are not to be construed as warranties or guarantees, express or implied, regarding the products or services described herein or their use or applicability. All sales are governed by our terms and conditions, which are available upon request. We reserve the right to modify or improve the designs or specifications of such products at any time without notice.

Emerson.com/FinalControl